## Sheet2
Transmission loss for month May'2019 of BSPTCL
220KV Level OU |  | 132KV level OU |  | Energy at 33 kv level
Energy Export at 220 kv level at Remote end (CTU/OU), received by BSPTCL (in MWH) | Energy Import at 220 kv level at remote end (CTU/OU), send by BSPTCL (in MWH) | Energy Export at 132 kv level at Remote end (CTU/OU/Consumer), received by BSPTCL (in MWH) | Energy Import at 132 kv level at remote end (CTU/OU/Consumer), send by BSPTCL (in MWH) | SST Consumption (in MWH) | Import from hydle, Rice Mill, Solar (in MWH) | Export to PSS, Solar, Hydle, Railway, Rice Mill (in MWH)
2309840.82 | 266551.2 | 1065597.0407 | 296934.1302 | 510.0987 | 12224.5583 | 2739923.0618
220 import from OU |  | 2309840.82 | A
220 Export to OU |  | 266551.2 | B
Net 220 in System |  | 2043289.62 | C= A-B
132 KV Import from OU |  | 1065597.0407 | D
132 KV Export to OU |  | 296934.1302 | E
Net 132 KV in System |  | 768662.9104 | F= D-E
33 KV import in system |  | 12224.5583 | G
33 KV SST Aux. Consumotion |  | 510.0987 | H
total power in system |  | 2824177.0888 | I= C+F+G
total 33 KV |  | 2739923.0618 | J
Loss |  | 83743.9283 | K= I-J-H
% loss |  | 2.472 | L = K/(A+D+G)*100
Note:- 1. All readings are in MWH.
2. OU Stand for Other Utility.
3. Energy reading taken of other(Remote) end, where line is ownered by BSPTCL.
4. Energy reading taken of BSPTCL(Local) end, where line is ownered by, other trans. Utilities.
5. In Patna(PG) reading of ICT-I,II&III has been taken which is availed by Gaurichak, Fatuha, & Khagaul
6. In Gaya(PG) reading of ICT-I,II&III has been taken which is availed by Dehri, Sonenagar, Bodhgaya & Khizirsarai(BGCL)
in which reaading of Khizirsarai(BGCL) is subtracted for Transmission loss calculation of BSPTCL.
7. In Darbhanga(DMTCL) reading of ICT-I&II has been taken which is availed by Motipur, Darbhanga(new), Laukahi &
Samastipur(new)
8. GSS having 33KV export is 0(zero), are cherged on no load.
9. Meter connection are applied for those GSS in which SST consumption is 0(zero).

## Sheet3
Transmission loss for month May'2019 of BSPTCL |  |  | Transmission loss for month May'2019 of BSPTCL |  |  | Transmission loss for month May'2019 of BSPTCL
GSS power received/Send, from/to, CTU/ Other Utility | 220KV Level OU |  | GSS power received/Send, from/to, CTU/ Other Utility | 132KV level OU |  | GSS power received/Send, from/to, PSS, Solar, Rice Mill, Hydle | Energy at 33 kv level
| Energy Export at 220 kv level at Remote end (CTU/OU), received by BSPTCL (in MWH) | Energy Import at 220 kv level at remote end (CTU/OU), send by BSPTCL (in MWH) |  | Energy Export at 132 kv level at Remote end (CTU/OU/Consumer), received by BSPTCL (in MWH) | Energy Import at 132 kv level at remote end (CTU/OU/Consumer), send by BSPTCL (in MWH) |  | SST Consumption (in MWH) | Import from hydle, Rice Mill, Solar (in MWH) | Export to PSS, Solar, Hydle, Railway, Rice Mill (in MWH)
Gaurichak(Patna PG) | 493344.97 |  | Hathidah (TSS) | 0 | 2705 | Katra 132/33 | 0 | 0 | 63336.07
Fatuha (Patna PG) |  |  | Fatuha | 0 | 4629.2 | Gaurichak 220/132/33 KV | 3.24 | 0 | 26816
Khagaul(Patna PG) |  |  | Khagaul 220/132/33 KV | 0 | 3001.44 | Masaudhi 132/33 | 4 | 0 | 13611
Khagaul(Ara (PG) |  | 6108 | Banjari 132/33 KV | 0 | 3810.4 | Gaighat 132/33 | 5.73 | 0 | 48050.59
Khagaul(Patna PG U BGCL) |  |  | Aurangabad 132/33 KV | 0 | 11758.1 | Mithapur 132/33 | 10.59 | 0 | 32025.24
Dehri-on-Son(Pusauli PG) | 47223 |  | Sonenagar (Rihand) | 0 | 20421 | Barh 132/33 | 0 | 0 | 18385.98
Dehri-on-Son(GAYA PG) | 360255 |  | Sonenagar (TSS) | 0 | 2387.5538 | Hathidah 132/33 | 0 | 0 | 14717
Sonenagar (Gaya PG) |  |  | Rafiganj (TSS) | 0 | 3362.7 | Fatuha | 2.67 | 0 | 44427.84
Bodhgaya(Gaya PG) |  |  | Rafiganj (Alfa Solar) | 3196 | 20 | Jakkanpur 132/33 | 7.6494 | 0 | 64806.24
Bodhgaya(K' Sarai BGCL) | 17938 | 2192 | Arrah (TSS) | 0 | 2020.27 | Karbigahia 132/33 | 0 | 0 | 44653.65
Pusauli (Pusauli PG) | 85822 |  | Arrah (PG) | 42400.032 | 0 | Digha (old) 132/33 | 12.83 | 0 | 50969.92
Pusauli (Ara PG) |  | 34676 | Jagdishpur (Ara PG) | 23758.128 | 0 | Bihta(old) 132/33 | 0 | 0 | 54419.43
Biharsarif (B'SarifPG) | 354854 |  | Dumraon (Ara PG) | 30077.76 | 0 | Bihta New 220/132/33 KV | 7.9 | 0 | 0
Biharsarif (K'Sarai BGCL) |  | 100170 | Dumraon (TSS) | 0 | 2338.4 | Khagaul 220/132/33 KV | 12.25 | 0 | 86027.54
Biharsarif (TTPS) | 92251 |  | Karmnasa (Chnd, Sahpr) | 2.88 | 22.56 | Dehri 220/132/33 KV | 3.974 | 0 | 25843.25
Biharsarif (BTPS) |  | 1752 | Karmnasa (Kudra TSS) | 58 | 0 | Banjari 132/33 KV | 12.454 | 0 | 11503.171
Begusarai Purnea(PG) | 8248.95 |  | Kudra (Pusauli PG) | 0 | 22231 | Bikramganj 132/33 KV | 2.43 | 0 | 27313.554
Kishanganj 220 | 186228 |  | Pusauli (Kudra TSS) | 0 | 23818 | Sasaram 132/33 KV | 4.808 | 0 | 23590.22
Hajipur ( Amnour BGCL) |  | 120821 | Mohaniya (Pusauli PG) | 20942 | 0 | Kochas 132/33 KV | 3.1 | 0 | 15809.268
Hajipur 220 (BTPS NTPC) | 2420 | 832.2 | Bodhgaya (TSS) | 0 | 2666.602 | Aurangabad 132/33 KV | 7.13 | 0 | 31308.95
Hajipur 220 (Kafeen PG) | 175875 |  | Bodhgaya (BGCL) | 0 | 2748.712 | Goh 132/33 KV | 10.54 | 0 | 8511
Motipur (MTPS) | 49132 |  | Sherghati (Solar) | 3922.699 | 20.009 | Sonenagar 132/33 KV | 14.86 | 1.1 | 21991.084
Motipur (DMTCL) | 225374.9 |  | Wazirganj (BGCL) | 12732 | 0 | Sonenagar 220/132/33 KV | 0 | 0 | 0
Darbhanga 220 (DMTCL) |  |  | Jahanabad (TSS) | 0 | 2172.8745 | Rafiganj 132/33 KV | 0 | 0 | 16975.8
Laukahi (DMTCL) |  |  | Hulasganj (BGCL) | 12013.9 | 0 | Arrah 132/33 KV | 0 | 0 | 39724.2 | cheack
Samastipur 220 (DMTCL) |  |  | Biharsharif (132 BGCL) | 882.3 | 6032 | Buxer 132/33 KV | 7.478 | 181.2 | 22136.3667 | cheack
Samastipur 220 (MTPS) | 19622 |  | Nalanda (Barhi) | 0 | 15.408 | Jagdishpur 132/33 KV | 4.74 | 0 | 23875.478
Gopalganj | 108400 |  | Nawada (BGCL) | 43948 | 0 | Piro 132/33 KV | 23.896 | 0 | 6985
Madhepura | 82852 |  | Rajgir (Barhi) | 0 | 0 | Dumraon 132/33 KV | 6.19 | 0 | 26194.896
Total | 2309840.82 | 266551.2 | Rajgir (Ord. Factory) | 0 | 357.2 | Karmnasa 132/33 KV | 2.67 | 0 | 15846.308
|  |  | Shiekhpura (BGCL) | 9289 | 0 | Ramgarh 132/33 KV | 1.79 | 0 | 6962
|  |  | Sabour (Banka PG) | 44425.044 | 0 | Bhabhua 132/33 KV | 7.37 | 0 | 1887.72
|  |  | Sabour (NTPC) | 1.8 | 0 | Kudra 132/33 KV | 0 | 0 | 11459
|  |  | Sabour (BGCL) | 0 | 0 | Pusauli 220/132/33 KV | 7.15 | 0 | 2649.4
|  |  | Sultanganj (Banka PG) | 52138 | 0 | Mohaniya 132/33 KV | 0 | 0 | 16106.2 | cheack
|  |  | Sultanganj (H.K.BGCL) | 155.2 | 23946.4 | Bodhgaya 220/132/33 KV | 0 | 0 | 43405.17
|  |  | Sultanganj(G.Dih BGCL) | 596 | 4722 | Sherghati 132/33 | 0 | 3836.7 | 13857
|  |  | Sultanganj (Deoghar) | 0 | 14.4 | Wazirganj 132/33 KV | 0 | 0 | 12604.68 | cheack
|  |  | Kahalgaon (NTPC) | 38039.4 | 0 | Imamganj 132/33 KV | 0 | 0 | 12270.3
|  |  | Kahalgaon (Lalmatiya) | 0 | 15852 | Chandauti 132/33 | 0 | 0 | 53513.2 | cheack
|  |  | Banka 132/33 | 34088.826 | 0 | Belaganj 132/33 KV | 6.3748 | 0 | 9129.3
|  |  | Naugachhia 132/33 | 186 | 914 | Tekari 132/33 KV | 2.75 | 0 | 11822.57
|  |  | Jamalpur 132/33 | 36579.4 | 0 | Jahanabad 132/33 | 0 | 0 | 20506.74
|  |  | Jamui (PG) | 47393.712 | 0 | Tehta 132/33 KV | 0 | 0 | 7932
|  |  | Jamui (TSS) | 0 | 4255.68 | Hulasganj 132/33 | 8.87 | 0 | 10513.37
|  |  | Lakhisarai (PG) | 51857.04 | 0 | Ataulah 132/33 | 0 | 0 | 22004.6
|  |  | Lakhisarai (TSS) | 0 | 4101.9 | Biharsharif | 7.96 | 0 | 0
|  |  | Lakhisarai (BGCL) | 0 | 5392 | Nalanda 132/33 | 2.83 | 0 | 16296
|  |  | Begusarai(BTPS) | 0 | 1360.9 | Ekangarsarai 132/33 | 0 | 0 | 22298
|  |  | Khagaria (BTPS) | 19560 | 0 | Harnaut 132/33 | 0 | 0 | 21977
|  |  | Khagaria (TSS) | 0 | 1533.28 | Baripahari 132/33 | 4.23 | 0 | 45148
|  |  | Purnea (PG) | 120277.6 | 0 | Nawada 132/33 | 0 | 1997.9333 | 41222.48
|  |  | Baisi 132/33 | 2241.5 | 0 | Warsaliganj 132/33 | 7.84 | 0 | 5431.5
|  |  | Kisanganj (Purnea PG) | 16616 | 0 | Rajgir 132/33 | 0 | 0 | 16061
|  |  | Muzaffarpur 132/33 | 76282 | 0 | Shiekhpura 132/33 | 0 | 0 | 21639
|  |  | SKMCH 132/33 KV | 57202.6667 | 0 | Sabour 132/33 | 0 | 0 | 43953.47 | cheack
|  |  | Motipur (MTPS) | 0 | 0 | Sultanganj 132/33 | 0 | 0 | 21145.57
|  |  | Motipur (TSS) | 0 | 681 | Kahalgaon 132/33 | 15.97 | 0 | 21993.121
|  |  | Hajipur (TSS) | 0 | 972.741 | Banka 132/33 | 0 | 3443.685 | 28688
|  |  | Vaishali (BRF) | 0 | 758.4 | BANKA NEW 132/33 KV | 0 | 0 | 1328.8
|  |  | Samastipur (MTPS) | 0 | 0 | Naugachhia 132/33 | 0 | 0 | 15563.2
|  |  | Samastipur (TSS) | 0 | 912 | Jamalpur 132/33 | 5.95 | 0 | 29933.3
|  |  | Dalsingh Sarai(TSS) | 0 | 2340 | Tarapur 132/33 | 0 | 0 | 7958
|  |  | Rosera(Sugar Mill) | 1065.33 | 101.04 | Jamui 132/33 | 0 | 0 | 29848.5125
|  |  | 132/33 Motihari | 34518.6 | 80.19 | Jamui (new) | 7.43 | 0 | 7523
|  |  | 132/33 Raxaul | 52500 | 33482 | Lakhisarai 132/33 | 0 | 0 | 28356.55
|  |  | 132/33 Betiah(DMTCL) | 70006 | 0 | Begusarai | 0 | 0 | 39675.5
|  |  | Ramnagar (BHPC) | 1095.936 | 8833.704 | Balaia 132/33 | 0 | 0 | 10377.5 | cheack
|  |  | Ramnagar (Sugar Mill) | 4.655 | 564.406 | Manjhaul 132/33 | 0 | 0 | 16448
|  |  | Chapra (BGCL) | 58979.552 | 0 | Teghra 132/33 KV | 2.75 | 0 | 100 | cheack
|  |  | Chapra (TSS) | 0 | 1717.89 | Khagaria 132/33 | 0 | 0 | 26008
|  |  | Sheetalpur 132/33 KV | 0 | 3009.6 | Bakhri 132/33 | 0 | 0 | 0
|  |  | 132/33 MASHRAKH | 0 | 345.2 | Purnea 132/33 | 0 | 0 | 47853.2
|  |  | Gopalganj 132/33 KV | 0 | 128.9 | Damdaha 132/33 | 0 | 0 | 546.3
|  |  | Siwan 132/33 KV | 46138.8 | 1392.9 | Banmankhi 132/33 | 0 | 0 | 8651.5
|  |  | Madhepura | 0 | 595.65 | Barsoi 132/33 | 0 | 0 | 11783
|  |  | Kataiya 132/33 KV | 425.28 | 62387.52 | Manihari 132/33 | 1.32 | 0 | 3393
|  |  | Total | 1065597.0407 | 296934.1302 | Katihar 132/33 | 9 | 0 | 23298.8
[6 empty] | Baisi 132/33 | 9 | 0 | 1846
[6 empty] | Kisanganj | 7.43 | 0 | 5263.2
[6 empty] | Kisanganj 132/33 | 9 | 0 | 16704 | cheack
[6 empty] | Forbisganj 132/33 | 3.2875 | 0 | 22293.7356
[6 empty] | Araria 132/33 | 7.47 | 0 | 11228.4875
[6 empty] | Muzaffarpur 132/33 | 2.37 | 0 | 48402.4 | cheack
[6 empty] | SKMCH 132/33 KV | 0 | 0 | 41993.4
[6 empty] | Motipur 220/132/33 KV | 0 | 0 | 11217
[6 empty] | Mushahari 220/132/33 | 0 | 0 | 18212
[6 empty] | Sitamari 132/33 | 4.753 | 0 | 30787.62
[6 empty] | Runnisaidpur 132/33 | 0 | 0 | 11269.8
[6 empty] | Belsand 132/33 | 0 | 0 | 2426
[6 empty] | Pupri 132/33 | 1.37 | 0 | 10968
[6 empty] | Sheohar 132/33 | 0 | 0 | 11105.4
[6 empty] | Hajipur 220 KV | 0 | 0 | 0
[6 empty] | Hajipur132/33 | 9.85 | 0 | 47375.941
[6 empty] | Vaishali 132/33 | 23.07 | 0 | 26660.27
[6 empty] | Jandaha | 0 | 0 | 24528.47
[6 empty] | Mahnar | 0 | 0 | 4806
[6 empty] | Samastipur 132/33 | 19.37 | 0 | 40763.925
[6 empty] | Samastipur new | 0 | 0 | 3841.37
[6 empty] | Sahpurpatori 132/33 KV | 0 | 0 | 0
[6 empty] | Dalsinghsarai | 3.01 | 0 | 17505.24
[6 empty] | Rosera | 0 | 0 | 8714
[6 empty] | Darbhanga (220) | 0 | 0 | 0
[6 empty] | Darbhanga 132/33 | 0 | 0 | 16346.4
[6 empty] | Gangwara 132/33 | 0 | 0 | 29549.945
[6 empty] | Kusheshwarsthan 132/33 | 0 | 0 | 12538.98
[6 empty] | Madhubani | 0 | 0 | 14159.428
[6 empty] | Pandaul | 0 | 0 | 19309.572
[6 empty] | Jainagar | 7.434 | 0 | 12418.1625
[6 empty] | Benipatti | 0 | 0 | 10361.934
[6 empty] | Phulparas | 0 | 0 | 14013.712
[6 empty] | Jhanjarpur | 0 | 0 | 3906.3
[6 empty] | Laukhai | 3.513 | 0 | 1000.5
[6 empty] | 132/33 Motihari | 1.437 | 0 | 33847.624
[6 empty] | 132/33 Dhaka | 0 | 0 | 19015.18
[6 empty] | 132/33 Pakdidyal | 1.053 | 0 | 1718.8
[6 empty] | Chakiya | 9.286 | 0 | 13061.1
[6 empty] | 132/33 Raxaul | 3.587 | 0 | 18884.73
[6 empty] | Areraj 132/33 KV | 25.213 | 0 | 9260.2
[6 empty] | 132/33 Betiah | 8.133 | 0 | 30979.89
[6 empty] | 132/33 Ramnagar | 0 | 1415.94 | 23567.25
[6 empty] | 132/33 Narkatiyaganj | 0 | 0 | 6321.2
[6 empty] | 132/33 Thakara | 0 | 1348 | 1162.56
[6 empty] | Chapra 132/33 KV | 0.551 | 0 | 27802.4
[6 empty] | Sheetalpur 132/33 KV | 0 | 0 | 12824.72
[6 empty] | 132/33 MASHRAKH | 0 | 0 | 16814.32
[6 empty] | Ekma 132/33 KV | 0 | 0 | 10191
[6 empty] | Gopalganj 132/33 KV | 4.73 | 0 | 41368.4
[6 empty] | Hathua 132/33 KV | 0.591 | 0 | 13850.6
[6 empty] | Siwan 132/33 KV | 0 | 0 | 43524.66
[6 empty] | Raghunathpur 132/33 KV | 0.067 | 0 | 10498.8
[6 empty] | Maharajganj 132/33 KV | 1.933 | 0 | 12253.2
[6 empty] | Madhepura | 6.182 | 0 | 17760 | cheack
[6 empty] | Udakisanganj | 1.135 | 0 | 13715.618
[6 empty] | Sahrsa 132/33 KV | 5.147 | 0 | 15460.65
[6 empty] | Sonbarsha | 0 | 0 | 7081.6
[6 empty] | Simri Bakhtiyarpur132/33 KV | 0 | 0 | 4545
[6 empty] | Raghopur 132/33 KV | 0 | 0 | 0
[6 empty] | Supaul 132/33 KV | 52.2 | 0 | 16932.83 |  | 2307420.82
[6 empty] | Kataiya 132/33 KV | 3.142 | 0 | 10048.938 |  | 265719
[6 empty] | Nirmali 132/33 KV | 1.57 | 0 | 2451 |  | 2305228.82
[6 empty] | Triveniganj | 2.5 | 0 | 2486 |  | 263527
| 2309840.82 | 266551.2 | 0 | 1065597.0407 | 296934.1302 | Total | 510.0987 | 12224.5583 | 2739923.0618 |  | 261775
GSS power received/Send, from/to, CTU/ Other Utility | 220KV Level OU |  | GSS power received/Send, from/to, CTU/ Other Utility | 132KV level OU |  | GSS power received/Send, from/to, PSS, Solar, Rice Mill, Hydle | Energy at 33 kv level
| Energy Export at 220 kv level at Remote end (CTU/OU), received by BSPTCL (in MWH) | Energy Import at 220 kv level at remote end (CTU/OU), send by BSPTCL (in MWH) |  | Energy Export at 132 kv level at Remote end (CTU/OU/Consumer), received by BSPTCL (in MWH) | Energy Import at 132 kv level at remote end (CTU/OU/Consumer), send by BSPTCL (in MWH) |  | SST Consumption (in MWH) | Import from hydle, Rice Mill, Solar (in MWH) | Export to PSS, Solar, Hydle, Railway, Rice Mill (in MWH)
| 2309840.82 | 266551.2 | 0 | 1065597.0407 | 296934.1302 | Total | 510.0987 | 12224.5583 | 2739923.0618
220 import from OU |  | 2309840.82 | A | 3387662.419
220 Export to OU |  | 266551.2 | B | 3303408.3921
Net 220 in System |  | 2043289.62 | C= A-B
132 KV Import from OU |  | 1065597.0407 | D
132 KV Export to OU |  | 296934.1302 | E
Net 132 KV in System |  | 768662.9104 | F= D-E
33 KV import in system |  | 12224.5583 | G
33 KV SST Aux. Consumotion |  | 510.0987 | H
total power in system |  | 2824177.0888 | I= C+F+G
total 33 KV |  | 2739923.0618 | J
Loss |  | 83743.9283 | K= I-J-H
% loss |  | 2.472 | L = K/(A+D+G)*100