## Aug 19
Transmission loss for month August'2019 of BSPTCL |  |  | Transmission loss for month August'2019 of BSPTCL |  |  | Transmission loss for month August'2019 of BSPTCL
GSS power received/Send, from/to, CTU/ Other Utility | 220KV Level OU |  | GSS power received/Send, from/to, CTU/ Other Utility | 132KV level OU |  | GSS power received/Send, from/to, PSS, Solar, Rice Mill, Hydle | Energy at 33 kv level
| Energy Export at 220 kv level at Remote end (CTU/OU), received by BSPTCL (in MWH) | Energy Import at 220 kv level at remote end (CTU/OU), send by BSPTCL (in MWH) |  | Energy Export at 132 kv level at Remote end (CTU/OU/Consumer), received by BSPTCL (in MWH) | Energy Import at 132 kv level at remote end (CTU/OU/Consumer) , send by BSPTCL (in MWH) |  | SST Consumption (in MWH) | Import from hydle, Rice Mill, Solar (in MWH) | Export to PSS, Solar, Hydle, Railway, Rice Mill (in MWH)
Gaurichak(Patna PG) | 466714 | 0 | Hathidah (TSS) | 0 | 2828 | Katra 132/33 | 10.422 | 0 | 56437.6083
Fatuha (Patna PG) |  | 0 | Fatuha(TSS) | 0 | 4856 | Gaurichak 220/132/33 KV | 0 | 0 | 33806.4
Khagaul(Patna PG) |  | 0 | Khagaul 220/132/33 KV(TSS) | 0 | 3231.84 | Masaudhi 132/33 | 8.152 | 0 | 22005
Khagaul(Ara (PG) | 0 | 40807.936 | Banjari 132/33 KV(KCL) | 0 | 4635.2 | Gaighat 132/33 | 4 | 0 | 46075.28 | Khagaul(Ara (PG) | 40807.936
Khagaul(Patna PG U BGCL) | 91631.68 | 0 | Aurangabad (SHREE CEMENT) | 0 | 10109.2 | Mithapur 132/33 | 5.32 | 0 | 31288.313
Dehri-on-Son(Pusauli PG) | 40254.544 | 0 | Sonenagar (Rihand) | 0 | 0 | Barh 132/33 | 0 | 0.095 | 17607.268
Dehri-on-Son(GAYA PG) | 439042 | 0 | Sonnagar (Japla) | 0 | 19589.624 | Hathidah 132/33 | 0 | 0 | 14332
Sonenagar (Gaya PG) |  | 0 | Sonenagar (TSS) | 0 | 2556.8333 | Fatuha | 0 | 0 | 45531.39
Bodhgaya(Gaya PG) |  | 0 | Rafiganj (TSS) | 0 | 4184.7 | Jakkanpur 132/33 | 0.92 | 0 | 56743.93
Bodhgaya(K' Sarai BGCL) | 853 | 0 | Rafiganj (Alfa Solar) | 2746 | 24 | Karbigahia 132/33 | 7.8144 | 0 | 41854
Pusauli (Pusauli PG) | 82865.168 | 0 | Arrah (TSS) | 0 | 1208.9333 | Digha (old) 132/33 | 0 | 0 | 49746.734
Pusauli (Ara PG) | 0 | 14552.272 | Arrah (PG) | 113192.102 |  | Bihta(old) 132/33 | 3.68 | 0 | 62367.5
Biharsarif (B'SarifPG) | 316064.8022 | 0 | Jagdishpur (Ara PG) |  |  | Bihta New 220/132/33 KV | 0 | 0 | 0
Biharsarif (K'Sarai BGCL) | 0 | 60620 | Dumraon (Ara PG) |  |  | Khagaul 220/132/33 KV | 0 | 0 | 89079.5182
Biharsarif (TTPS) | 107519.1 | 0 | Dumraon (TSS) | 0 | 2436.6 | Dehri 220/132/33 KV | 0 | 543.7667 | 26829.4493
Biharsarif (BTPS) | 0 | 32720 | Karmnasa (Chnd, Sahpr) | 0 | 15.0444 | Banjari 132/33 KV | 0 | 0 | 15704.2
Begusarai Purnea(PG) | 59695.936 | 0 | Karmnasa (Kudra TSS) | 0 | 0 | Bikramganj 132/33 KV | 13.17 | 0 | 28518.6
Kishanganj 220 | 181509.056 | 0 | Kudra (Pusauli PG) | 0 | 20120.7996 | Sasaram 132/33 KV | 0 | 0 | 25252.28
Hajipur ( Amnour BGCL) | 0 | 130104 | Pusauli (Kudra TSS) | 0 | 27599 | Kochas 132/33 KV | 4.646 | 0 | 17247.9
Hajipur 220 (BTPS NTPC) | 27860 | 200 | Mohaniya (Pusauli PG) | 18833.8932 | 0 | Aurangabad 132/33 KV | 0 | 0 | 35075.7
Hajipur 220 (Kafeen PG) | 166489.616 | 0 | Bodhgaya (TSS) | 0 | 2678.486 | Goh 132/33 KV | 0 | 0 | 13058
Motipur (MTPS) | 55175 | 0 | Bodhgaya (BGCL) | 18241 | 511 | Sonenagar 132/33 KV | 0 | 0 | 27411.619
Motipur (DMTCL) | 250030.7946 | 0 | Sherghati (Solar) | 3123.087 | 19.635 | Sonenagar 220/132/33 KV | 0 | 0 | 96
Darbhanga 220 (DMTCL) |  | 0 | Wazirganj (BGCL) | 14885 | 0 | Rafiganj 132/33 KV | 0 | 0 | 17527.2
Laukahi (DMTCL) |  | 0 | Jahanabad (TSS) | 0 | 2161.677 | Arrah 132/33 KV | 0 | 0 | 43083.6333
Samastipur 220 (DMTCL) |  | 0 | Hulasganj (BGCL) | 16304 | 0 | Buxer 132/33 KV | 0 | 67.05 | 25274.5167
Samastipur 220 (MTPS) | 6400 | 0 | Biharsharif (132 BGCL) | 1083 | 1402 | Jagdishpur 132/33 KV | 8.122 | 0.5 | 28721.5
Gopalganj(MTPS) | 116370 | 0 | Nalanda (Barhi) | 0 | 0 | Piro 132/33 KV | 0 | 0 | 7855
Madhepura (Purnea PG) | 82933.92 | 0 | Nawada (BGCL) | 51547.9 | 0 | Dumraon 132/33 KV | 20.724 | 0 | 34255
Total | 2491408.6168 | 279004.208 | Rajgir (Barhi) | 0 | 0 | Karmnasa 132/33 KV | 0 | 0 | 20557.961
|  |  | Rajgir (Ord. Factory) | 0 | 287.5 | Ramgarh 132/33 KV | 0 | 0 | 10819
|  |  | Shiekhpura (BGCL) | 5230 | 0 | Bhabhua 132/33 KV | 0 | 0 | 5712.24
|  |  | Sabour(BGCL) | 0 | 0 | Kudra 132/33 KV | 5.3 | 0 | 10919
|  |  | Sabour(NTPC) | 2802 | 0 | Pusauli 220/132/33 KV | 0 | 0 | 6844.6
|  |  | Sabour (Banka PG) | 170524.4462 |  | Mohaniya 132/33 KV | 0 | 0 | 19499.2
|  |  | Banka 132/33(Banka PG) |  |  | Bodhgaya 220/132/33 KV | 0 | 0 | 44886.83
|  |  | Sultanganj (Banka PG) |  |  | Sherghati 132/33 | 0 | 3035.4 | 15492.4
|  |  | Sultanganj (Jamalpur BGCL) | 0 | 35861 | Wazirganj 132/33 KV | 0 | 0 | 14628
|  |  | Sultanganj (G' Dih BGCL) | 0 | 5076 | Imamganj 132/33 KV | 1.2 | 0 | 12816.6
|  |  | Sultanganj (Deoghar) | 0 | 16.416 | Chandauti 132/33 | 4.56 | 0 | 52246.8
|  |  | Kahalgaon (NTPC) | 29430.6 | 0 | Belaganj 132/33 KV | 0 | 0 | 12940
|  |  | Kahalgaon (Lalmatiya) | 0 | 17167.104 | Tekari 132/33 KV | 9.3 | 0 | 15320.6
|  |  | Naugachhia 132/33(BTPS) | 228 | 496 | Jahanabad 132/33 | 3.1 | 0 | 27517.3775
|  |  | Jamalpur 132/33(BGCL) | 42239.1 | 0 | Tehta 132/33 KV | 0 | 0 | 10233.6
|  |  | Jamui (TSS) | 0 | 1606.56 | Hulasganj 132/33 | 0 | 0 | 15603.5
|  |  | Jamui (Lakhisarai PG) | 110461.5232 |  | Ataulah 132/33 | 8.534 | 0 | 27839.2
|  |  | Lakhisarai (Lakhisarai PG) |  |  | Biharsharif | 0 | 0 | 342.2
|  |  | Lakhisarai (TSS) | 0 | 4516.71 | Nalanda 132/33 | 6.12 | 0 | 18237.8
|  |  | Lakhisarai (BGCL) | 0 | 6017 | Ekangarsarai 132/33 | 0 | 0 | 29904
|  |  | Begusarai(BTPS) | 0 | 22087 | Harnaut 132/33 | 0 | 0 | 28127.8
|  |  | Khagaria (BTPS) | 23763.96 | 0 | Baripahari 132/33 | 8.9 | 0 | 51077.4
|  |  | Khagaria (TSS) | 0 | 1740.44 | Nawada 132/33 | 9.794 | 1651 | 40300.971
|  |  | Purnea (Purnea PG) | 150158.116 |  | Warsaliganj 132/33 | 0 | 0 | 15271.5
|  |  | Kisanganj (Purnea PG) |  |  | Rajgir 132/33 | 0 | 0 | 20634
|  |  | Baisi 132/33(Dalkola) | 3081.204 | 0 | Shiekhpura 132/33 | 7.53 | 0 | 26719.5
|  |  | Samastipur (TSS) | 0 | 1031 | Sabour 132/33 | 0 | 0 | 46642.2
|  |  | Samastipur 132/33 (KBUNL) | 131277 |  | Sultanganj 132/33 | 0 | 0 | 28535.7
|  |  | Muzaffarpur 132/33(KBUNL) |  |  | Kahalgaon 132/33 | 13.585 | 0 | 25206.3
|  |  | SKMCH 132/33 KV(KBUNL) |  |  | Banka 132/33 | 0 | 3036.675 | 23513.542
|  |  | Motipur 220/132/33(KBUNL) |  |  | BANKA NEW 132/33 KV | 0 | 0 | 7348
|  |  | Motipur (TSS) | 15 | 1445 | Naugachhia 132/33 | 0 | 0 | 18300
|  |  | Hajipur (TSS) | 0 | 1064.958 | Jamalpur 132/33 | 1.88 | 0 | 30559.5
|  |  | Vaishali (BRF) | 0 | 3100.8 | Tarapur 132/33 | 0 | 0 | 10738
|  |  | Dalsingh Sarai(TSS) | 0 | 2920 | Jamui 132/33 | 0 | 0 | 34466.9625
|  |  | Rosera(Sugar Mill) | 0 | 91.21 | Jamui (new) | 0 | 0 | 8786.2
|  |  | Motihari(Sugauli Sugar Mill) | 0.0666 | 58.1418 | Lakhisarai 132/33 | 0 | 0 | 28983.55
|  |  | 132/33 Motihari(DMTCL) | 143127.2466 |  | Begusarai | 0 | 0 | 35631.5
|  |  | 132/33 Betiah(DMTCL) |  |  | Balaia 132/33 | 1.74 | 0 | 11554
|  |  | 132/33 Raxaul(DMTCL) |  |  | Manjhaul 132/33 | 8.87 | 0 | 15875.5
|  |  | 132/33 Raxaul(PARWANIPUR) | 836 | 16344 | Teghra 132/33 KV | 0 | 0 | 644
|  |  | Ramnagar (BHPC) | 1733.16 | 1767.36 | Khagaria 132/33 | 0 | 0 | 26783.6
|  |  | Ramnagar (Sugar Mill) | 0 | 605.611 | Bakhri 132/33 | 0 | 0 | 2610.2
|  |  | Chapra (BGCL) | 60226.5 | 0 | Purnea 132/33 | 0 | 0 | 50539.8
|  |  | Chapra (TSS) | 0 | 1762.9163 | Damdaha 132/33 | 6.72 | 0 | 7938.5
|  |  | Sheetalpur 132/33 KV | 0 | 1598.4 | Banmankhi 132/33 | 3.88 | 0 | 10962.5
|  |  | 132/33 MASHRAKH(DLF) | 0 | 329.6 | Barsoi 132/33 | 0 | 0 | 10661.8
|  |  | Gopalganj KV(SUGAR MILL) | 0 | 107 | Manihari 132/33 | 0 | 0 | 5246
|  |  | Siwan 132/33 KV(BGCL) | 47907 | 0 | Katihar 132/33 | 0 | 0 | 25529.3
|  |  | Siwan 132/33 KV(TSS) | 0 | 1454.55 | Baisi 132/33 | 12.54 | 0 | 3081
|  |  | Madhepura(RAILWAY FAC) | 0 | 645.9 | Kisanganj220/132/33 | 6.43 | 0 | 8738.8
|  |  | Kataiya 132/33 KV | 3986 | 24339 | Kisanganj 132/33 | 16 | 0 | 22273.33
|  |  | Total | 1166982.9048 | 263705.7496 | Forbisganj 132/33 | 0 | 0 | 28683.149
[6 empty] | Araria 132/33 | 2.3625 | 0 | 14469.5
[6 empty] | Muzaffarpur 132/33 | 11.3 | 0 | 53672.8
[6 empty] | SKMCH 132/33 KV | 9.11 | 0 | 44084
[6 empty] | Motipur 220/132/33 KV | 0 | 0 | 13276.1
[6 empty] | Mushahari 220/132/33 | 6.2 | 0 | 16688
[6 empty] | Sitamari 132/33 | 8.41 | 0 | 35276.82
[6 empty] | Runnisaidpur 132/33 | 3.13 | 0 | 11711.28
[6 empty] | Belsand 132/33 | 0 | 0 | 2540.5
[6 empty] | Pupri 132/33 | 0 | 0 | 13537
[6 empty] | Sheohar 132/33 | 0 | 0 | 12971
[6 empty] | Hajipur 220 KV | 9.2 | 0 | 0
[6 empty] | Hajipur132/33 | 6.8 | 0 | 44368.2116
[6 empty] | Vaishali 132/33 | 5.8 | 0 | 26423.381
[6 empty] | Jandaha | 3.27 | 0 | 24405.6
[6 empty] | Mahnar | 0 | 0 | 6007.5
[6 empty] | Samastipur 132/33 | 2.43 | 0 | 38749.39
[6 empty] | Samastipur new220/132/33 | 6.47 | 0 | 4821
[6 empty] | Sahpurpatori 132/33 KV | 0 | 0 | 4679.5
[6 empty] | Dalsinghsarai | 8.3 | 0 | 16912.512
[6 empty] | Rosera | 0 | 0 | 12116
[6 empty] | Darbhanga (220) | 0 | 0 | 0
[6 empty] | Darbhanga 132/33 | 11.3 | 0 | 15321.9
[6 empty] | Gangwara 132/33 | 16.61 | 0 | 31716
[6 empty] | Kusheshwarsthan 132/33 | 0 | 0 | 13506.204
[6 empty] | Madhubani | 0 | 0 | 15228.816
[6 empty] | Pandaul | 0 | 0 | 21565.93
[6 empty] | Jainagar | 0 | 0 | 13460.6755
[6 empty] | Benipatti | 2.313 | 0 | 11168
[6 empty] | Phulparas | 0 | 0 | 13804
[6 empty] | Jhanjarpur | 0 | 0 | 3707.6
[6 empty] | Laukhai | 0 | 0 | 4874.4
[6 empty] | 132/33 Motihari | 18.292 | 0 | 35743.94
[6 empty] | 132/33 Dhaka | 11.0002 | 0 | 23476.5258
[6 empty] | 132/33 Pakdidyal | 0 | 0 | 1931.6
[6 empty] | Chakiya | 8 | 0 | 14216.4
[6 empty] | 132/33 Raxaul | 6.7 | 0 | 20413.496
[6 empty] | Areraj 132/33 KV | 0 | 0 | 11679.4
[6 empty] | 132/33 Betiah | 0 | 0 | 31851.45
[6 empty] | 132/33 Ramnagar | 8.42 | 1074.576 | 27532.383
[6 empty] | 132/33 Narkatiyaganj | 0 | 0 | 7599.8
[6 empty] | 132/33 Thakara | 4.9 | 1385.8 | 1067.4
[6 empty] | Chapra 132/33 KV | 0 | 0 | 26908.416
[6 empty] | Sheetalpur 132/33 KV | 8.8198 | 0 | 15281.89
[6 empty] | 132/33 MASHRAKH | 0 | 0 | 16272.558
[6 empty] | Ekma 132/33 KV | 3.488 | 0 | 10235.18
[6 empty] | Gopalganj 132/33 KV | 3.24 | 0 | 44335.196
[6 empty] | Hathua 132/33 KV | 7.869 | 0 | 15719.2
[6 empty] | Siwan 132/33 KV | 14.2009 | 0 | 43978.96
[6 empty] | Raghunathpur 132/33 KV | 0 | 0 | 13271.6
[6 empty] | Maharajganj 132/33 KV | 3.44 | 0 | 13012.6
[6 empty] | Madhepura | 0 | 0 | 20238.4
[6 empty] | Udakisanganj | 12.623 | 0 | 17382.966
[6 empty] | Sahrsa 132/33 KV | 9.0403 | 0 | 21208.1
[6 empty] | Sonbrsha | 3.5 | 0 | 8882.8
[6 empty] | Simri Bakhtiyarpur132/33 KV | 0 | 0 | 5707.4
[6 empty] | Raghopur 132/33 KV | 0 | 0 | 6468
[6 empty] | Supaul 132/33 KV | 13.8056 | 0 | 19778.184
[6 empty] | Kataiya 132/33 KV | 6.07 | 0 | 10875.727
[6 empty] | Nirmali 132/33 KV | 2.26 | 0 | 3091
[6 empty] | Triveniganj | 3.12 | 0 | 5102
Total | 2491408.6168 | 279004.208 | Total | 1166982.9048 | 263705.7496 | Total | 484.7477 | 10794.8627 | 3031436.7447
220 import from OU |  | 2491408.6168
220 Export to OU |  | 279004.208
Net 220 in System |  | 2212404.4088
132 KV Import from OU |  | 1166982.9048
132 KV Export to OU |  | 263705.7496 | 3669186.3843
Net 132 KV in System |  | 903277.1552 | 3574146.7023
33 KV import in system |  | 10794.8627 | 484.7477
33 KV SST Aux. Consumotion |  | 484.7477 | 94554.9342
total power in system |  | 3126476.4266 | 2.577
total 33 KV |  | 3031436.7447
Loss |  | 94554.9342
% loss |  | 2.577

## Sheet1
Transmission loss for month August' 2019 of BSPTCL
220KV Level OU |  | 132KV level OU |  | Energy at 33 kv level
Energy Export at 220 kv level at Remote end (CTU/OU), received by BSPTCL (in MWH) | Energy Import at 220 kv level at remote end (CTU/OU), send by BSPTCL (in MWH) | Energy Export at 132 kv level at Remote end (CTU/OU/Consumer), received by BSPTCL (in MWH) | Energy Import at 132 kv level at remote end (CTU/OU/Consumer), send by BSPTCL (in MWH) | SST Consumption (in MWH) | Import from hydle, Rice Mill, Solar (in MWH) | Export to PSS, Solar, Hydle, Railway, Rice Mill (in MWH)
2491408.6168 | 279004.208 | 1166982.9048 | 263705.7496 | 484.7477 | 10794.6727 | 3031436.7447
220 import from OU |  | 2491408.6168 | A |  | 3669186.1943
220 Export to OU |  | 279004.208 | B |  | 3574146.7023
Net 220 in System |  | 2212404.4088 | C= A-B |  | 484.7477
132 KV Import from OU |  | 1166982.9048 | D |  | 94554.7442
132 KV Export to OU |  | 263705.7496 | E |  | 2.577
Net 132 KV in System |  | 903277.1552 | F= D-E
33 KV import in system |  | 10794.6727 | G
33 KV SST Aux. Consumotion |  | 484.7477 | H
total power in system |  | 3126476.2366 | I= C+F+G
total 33 KV |  | 3031436.7447 | J
Loss |  | 94554.7442 | K= I-J-H
% loss |  | 2.577 | L = K/(A+D+G)*100
Note:- 1. All readings are in MWH.
2. OU Stand for Other Utility.
3. Energy reading taken of other(Remote) end, where line is ownered by BSPTCL.
4. Energy reading taken of BSPTCL(Local) end, where line is ownered by, other trans. Utilities.
5. In Patna(PG) reading of ICT-I,II&III has been taken which is availed by Gaurichak, Fatuha, & Khagaul
6. In Gaya(PG) reading of ICT-I,II&III has been taken which is availed by Dehri, Sonenagar, Bodhgaya & Khizirsarai(BGCL)
in which reaading of Khizirsarai(BGCL) is subtracted for Transmission loss calculation of BSPTCL.
7. In Darbhanga(DMTCL) reading of ICT-I&II has been taken which is availed by Motipur, Darbhanga(new), Laukahi &
Samastipur(new)
8. GSS having 33KV export is 0(zero), are cherged on no load.
9. Meter connection are applied for those GSS in which SST consumption is 0(zero).

## Sheet2
Transmission loss of BSPTCL
A | Total losses in the Transmission system | June'19 | July'19 | August'19
1 | Total energy delivered by CTU/ Inter state tie link/ Transmission licence at the interface point of intra-state Transmission System | 3344355.376 | 3221390.7173 | 3669186.1943
2 | Sum of all Energy delivered by the Transmission system to CTU/consumer/ state distribution system | 3262509.2593 | 3139840.3352 | 3574146.7023
3 | 33KV Auxiliary consumption in System (SST) | 450.5961 | 469.0202 | 484.7477
4 | Transmission loss in System (A1-A2-A3) | 81395.5206 | 81081.3619 | 94554.7442
5 | Transmission loss in (Transco) System (%) [A4/A1*100] | 2.4338 | 2.517 | 2.577